EXPERIMENT 1

COMPUTATION OF PARAMETERS AND MODELLING OF TRANSMISSION LINES

1.1 AIM

(i) To determine the positive sequence line parameters L and C per phase per kilometer of a three phase single and double circuit transmission lines for different conductor arrangements.

(ii) To understand modelling and performance of short, medium and long lines.

1.2 OBJECTIVES

i. To become familiar with different arrangements of conductors of a three phase single and double circuit transmission lines and to compute the GMD and GMR for different

arrangements.

ii. To compute the series inductance and shunt capacitance per phase, per km of a three phase single and double circuit overhead transmission lines with solid and bundled conductors.

iii. To become familiar with per phase equivalent of a three phase short and medium lines and to evaluate the performances for different load conditions.

iv. (a) To become familiar with the theory of long transmission line and study the effect of distributed parameters on voltage and currents, along the line, (b) calculate the surge

Impedance and surge impedance loading.

Three Phase - Symmetrical Spacing:

Three Phase - Asymmetrical Transposed:

Nominal П-Model

Bundle conductors

Equivalent П-Model

1 EXERCISES:

1.1       A three-phase transposed line composed of one ACSR, 1,43,000 cmil, 47/7 Bobolink conductor per phase with flat horizontal spacing of 11m between phases a and b and between phases b and c. The conductors have a diameter of 3.625 cm and a GMR of

1.439 cm. The line is to be replaced by a three conductor bundle of ACSR 477,000-cmil,

26/7 Hawk conductors having the same cross sectional area of aluminum as the single conductor line. The conductors have a diameter of 2.1793 cm and a GMR of 0.8839 cm.

The new line will also have a flat horizontal configurations, but it is to be operated at a

Higher voltage and therefore the phase spacing is increased to 14m as measured from the

Centre of the bundles. The spacing between the conductors in the bundle is 45 cm.

(a) Determine the inductance and capacitance per phase per kilometer of the above two

Lines.

(b) Verify the results using the available program.

(c) Determine the percentage change in the inductance and capacitance in the bundle

Conductor system. Which system is better and why?

1.2   A single circuit three phase transposed transmission line is composed of four ACSR 1,272,000 cmil conductors per phase with flat horizontal spacing of 14 m between

Phases a and b and between phases b and c. The bundle spacing is 45 cm. The

Conductor diameter is 3.16 cm.

a) Determine the inductance and capacitance per phase per kilometer of the line.

b) Verify the results using available program.

1.3 A 345 kV double circuit three phase transposed line is composed of two ACSR,

1,431,000 cmil, 45/7 bobolink conductors per phase with vertical conductor configuration

as shown in Fig. 1.13. The conductors have a diameter of 1.427 in and the bundle spacing

is 18 in.

a) Find the inductance and capacitance per phase per kilometer of the line.

b) Verify the results using the available program.

c) If we change the relative phase position to acb-a’b’c’, determine the inductance and

Capacitance per unit length using available program.

d) Which relative phase position is better and why?

1.4 A 230 kV, 60 HZ three phase transmissions is 160 km long. The per phase resistance is 0.124 Ω per km and the reactance is 0.497 Ω per km and the shunt admittance is 3.30 x 10-6∟900seimens per km It delivers 40MW at 220 KV with 0.9 power factor lagging. Use medium line П model

i. Determine the voltage and current at sending end and also compute voltage

regulation and efficiency.

ii. Verify the results using the available program

1.5 A three phase transmission line has a per phase impedance of  Z=0.03+j0.04 Ω per km and a per phase shunt admittance of y=j4.0 x 10-6   Simens per km. The line is 200

km long. Obtain ABCD parameters of the transmission line. The line is sending 407 MW

and 7.833 MVAR at 350KV.Use medium П model

1.6 A three phase 50 Hz, 400 kV transmission line is 250 km long. The line parameters per phase per unit length are found to be

r=0.02 Ω/km     L=1.06mH/km         C=0.011 µF/km

Determine the following using the program available use long line model.

(a) The sending end voltage, current and efficiency when the load at the receiving end is

640 MW at 0.8 power factor logging at 400 kV.

(b) The receiving end voltage, current, efficiency and losses when 480 MW and 320

MVAR are being transmitted at 400 kV from the sending end.

c) The sending end voltage, current and efficiency and losses when the receiving end load

Impedance is 230 Ω at 400KV

(d)  The receiving end voltage when the line is open circuited and is energized with                                                                                                                                       400kV at the sending end. Also, determine the reactance and MVAR of a three phase   shunt reactor to be installed at the receiving end in order to limit the no load receiving end voltage to 400 kV.

(e) The MVAR and capacitance to be installed at the receiving end for the loading

Condition in (a) to keep the receiving end voltage at 400 kV when the line is

Energized with 400 kV at the sending end.

(f) The line voltage profile along the line for the following cases: no load, rated load of

800 MW at 0.8 power factor at sending end at 400 kV, line terminated in the SIL and

Short circuited line.

EXPERIMENT 2

FORMATION OF BUS ADMITTANCE AND IMPEDANCE MATRICES AND SOLUTION OF NETWORKS

To understand the formation of network matrices, the bus admittance matrix Y and the bus impedance

2.1  AIM

solution using these matrices.

matrix Z of a power network, to effect certain required changes on these matrices and to obtain network

2.2  OBJECTIVES

i.     To write a computer program to form bus admittance matrix Y, given the impedances of

1. Using a text editor create an input file in the sequence given below for formation of

the elements of a power network and their connectivity (mutual coupling between elements

neglected)

ii.    To modify the matrix Y to effect specified changes in the configuration of the network.

iii.   To obtain network solution, that is, to determine the bus voltages given bus current injections.

iv.   To obtain certain specified columns of the bus impedance matrix Z or the full matrix Z using the

factors of Y or the inverse of Y.

Y and Z matrix for the 6-bus system. Check the results obtained using the available  Software. Run the program  and print the modified Y matrix for the 6 bus system for the removal

of the following components, one at-a-time:

- Line 4-6

- Transformer 4-3

##### SYSTEM DATA

NO OF BUSES            	            :   6           NO OF TRANSMISSION LINES:    5

NO OF TRANSFORMERS     :    2          NO OF SHUNT ELEMENTS    :    2

SYSTEM BASE MVA             :   100.00

TRANSMISSION LINE DATA

| L NO | S BUS | R BUS | R_IN_PU | X_IN_PU | HBC_IN_PU | RAT |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 1 | 6 | .1230 | .5180 | .0000 | 55.0000 |
| 2 | 1 | 4 | .0800 | .3700 | .0000 | 65.0000 |
| 3 | 4 | 6 | .0870 | .4070 | .0000 | 30.0000 |
| 4 | 5 | 2 | .2820 | .6400 | .0000 | 55.0000 |
| 5 | 2 | 3 | .7230 | 1.0500 | .0000 | 40.0000 |

TRANSFORMER DATA

| TNO | S BUS | R BUS | R_IN_PU | X_IN_PU | TAP_IN_PU | RAT |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 6 | 5 | .0000 | .3000 | 1.0000 | 30.0000 |
| 2 | 4 | 3 | .0000 | 1330 | 1.0000 | 55.0000 |

SHUNT CAP/REACTOR DATA

| S NO | BUS NO | SHUNT_MVAR |
| --- | --- | --- |
| 1 | 4 | 2.0000 |
| 2 | 6 | 2.5000 |

EXPERIMENT 3

LOAD FLOW ANALYSIS - I: SOLUTION OF LOAD FLOW AND RELATED PROBLEMS USING GAUSS-SEIDEL METHOD

AIM

(i)  To understand, the basic aspects of steady state analysis of power systems that are                                         required for effective planning and operation of power systems.

(ii) To understand, in particular, the mathematical formulation of load flow model in complex form and a simple method of solving load flow problems of small sized system using Gauss-Seidel iterative algorithm

OBJECTIVES

i. To write a computer program to solve the set of non-linear load flow equations using Gauss-Seidel Load Flow (GSLF) algorithm and present the results in the format required for system studies.

ii. To investigate the convergence characteristics of GSLF algorithm for normally loaded small system for different acceleration factors.

iii. To investigate the effects on the load flow results, load bus voltages and line transformer loadings, due to the following control actions:

a. Variation of voltage settings of P-V buses

b. Variation of shunt compensation at P-Q buses

c. Variation of tap settings of transformer

d. Generation shifting or rescheduling.

INPUT FILE:

POWER FLOW ANALYSIS I: SOLUTION OF POWER FLOW RELATED PROBLEMS BY GAUSS-SEIDEL

CASE:1   6-BUS SYSTEM-BASE CASE-POOR VOLTAGE PROFILE:

ACCN FACTOR=1

NAME:

ROLL NO:

VII SEMESTER

DATE:

6 2  4 5 2 1 2 100 100.00  .0001  1.0000

1     0.0000     .0000     .0000       0.0        0.00     1.020

2   50.0000     .0000     .0000   100.0    -20.00     1.020

3   55.000   13.000    1.000

4    0.000      0.000    1.000

5   30.000   18.000    1.000

6   50.000    5.000     1.000

1 1 6  0.1230  0.518 0.000 55.0

2 1 4  0.0800  0.370 0.000 65.0

3 4 6  0.0870  0.407 0.000 30.0

4 5 2  0.2820  0.640 0.000 55.0

5 2 3  0.7230  1.050 0.000 40.0

1 4 3  0.0000  0.1330 1.000 30.0

2 6 5  0.0000  0.3000 1.000 55.0

1 4  2.0

2 6  2.5

EXPERIMENT 4

PROBLEMS USING NEWTON-RAPHSON AND FAST DECOUPLED

METHOD

AIM:

(i} To understand the following for medium and large scale power systems.

a)	Mathematical formulation of load flow problem in real variable form.

b)	Newton Raphson method of load flow (NRLF) solution.

c)	Fast decoupled method of load flow (FDLP) solution.

(ii) To become proficient in the usage of software for practical problem solving in the

areas of power system planning and operation.

(iii) To become proficient in the usage of software in solving problems using Newton-

Raphson and Fast decoupled load flow methods.

OBJECTIVES:

- To investigate the convergence characteristics of load flow solutions using NRLF and FDLP algorithms for different sized systems and compare the same with that of GSLF algorithm.

- To investigate the effect of variation of voltage control  parameters such as generator voltage magnitude setting, off nominal tap ratio of transformer and MVAR injections of shunt capacitors/inductor on the voltage profile and transmission loss of the system.

- To assess the effect of single outage contingencies such as a line outages and generator outages.

- To investigate the convergence of load flow solution of a two bus system for different load conditions, understand the existence of maximum load ability condition and to verify the both, numerically (using load flow package) analytically using the two bus system equations.

EXERCISE:

- Obtain the load flow solution for the given 6 bus 5 line power system shown in experiment 2 using NRLF method using AU POWER LAB SOFTWARE.

EXPERIMENT 5

FAULT ANALYSIS

AIM:

To become familiar with modeling and analysis of power system under faulted condition and to compute the fault level post fault voltage and current for different types of fault both symmetrical and unsymmetrical.

OBJECTIVES:

- To carryout fault analysis for symmetrical and unsymmetrical faults in small systems using the Thevenin’s equivalent circuit in the sequences and phase domains at the faulted bus but without the use of software.

- To conduct fault analysis on a given system using software available and obtain fault analysis report with fault level and current at the faulted point and post-fault voltages and currents in the network for the following faults                                                                                                                   (a) Three-phase-to-ground

(b) Line-to-ground

(c) Line-to-Line

(d) Double-line-to-ground

- To study the variation in fault levels and currents in the system when it is interconnected to neighboring systems.

EXERCISE:

- It is proposed to conduct fault analysis on two alternative configurations of 4-bus system given in fig shown below.

G1, G2:  100MVA, 20KV, x+ = x- =xd” = 20%; x0=4%; xn = 5%

T1, T2: 100MVA, 20KV/345KV; xleak = 8%

L1, L2:  x+=x-=15%; x0=50% on the base of 100MVA

The first configuration, case (a), comprises star-star transformers and the second configuration, case (b), comprises star-delta transformers.

- For a three phase to ground (solid) fault, line to line fault, line to ground fault, double line to ground fault at bus 4, determine the fault current and MVA at faulted bus, post fault bus voltages, fault current distribution in different elements of the network using Thevenin equivalent circuit. Draw a single-line diagram showing the above results.

- Check the results obtained in (i) using available fault analysis software.

The 4-bus system in (i) above is interconnected to a neighboring system at tie bus 5, through a tie-line 3-5, whose parameters are the same as that of lines L1 and L2. The fault level at bus 5 in the neighboring system is 500MVA. Recompute the fault distribution in different elements of the network using available software.

2.  (i) For the system given in the figure apply a line-to-ground (solid) fault at bus 4 and determine the fault current and fault MVA at faulted bus, post-fault bus voltages and fault current contribution by each generator, both in sequences and phase domain using the available software.

(ii) Check the fault current at bus 4 computed in (i) above using Thevenin equivalent and the respective sequence network connection.

EXPERIMENT 6

TRANSIENT AND SMALL SIGNAL STABILITY ANALYSIS OF

SINGLE-MACHINE INFINITE BUS SYSTEM

AIM :

To become familiar with various aspects of the transient and small signal stability analysis of Single-Machine Infinite Bus (SMIB) system.

OBJECTIVES :

(i)   To understand modeling and analysis of transient and small signal stability of a SMIB power system.

(ii)   To examine the transient stability of a SMIB and determine the critical clearing time of the system through simulation by trial and error.

(iii)   To determine transient stability margin (MW) for different fault conditions.

(iv)   To obtain linearised swing equation and to determine the roots of        characteristic equation , damped frequency of oscillation and undamped natural     frequency.

EXERCISE :

(i)     A power system comprising a thermal generating plant with four 555 MVA,

24kV, 60HZ units supplies power to an infinite bus through a transformer and two transmission lines. The data for the system in p.u on a base of 2220 MVA, 24 kV is given below. An equivalent generator representing the 4 units, characterized by classical model:

Xd’ = 0.3 p.u     H= 3.5 MW-s/MVA            Transformer : X = 0.15 p.u

Line 1 : X = 0.5 p.u                     Line 2 : X = 0.93 p.u

Plant operating condition:      P = 0.9 p.u ; pf= 0.9(lag) ; Et = 1.0 p.u

It is proposed to examine the transient stability of the system for a three-phase-to ground fault at the end of line 2 near H.T bus occurring at time t= 0 sec. The fault is cleared at 0.07 sec. by simultaneous opening of the two circuit breakers at both the ends of line 2.(case1)

(a) Calculate the initial conditions necessary for the classical model of the

machine for the above pre-fault operating condition, determine the

critical clearing angle and time for the fault using “Equal Area Criterion”

and hence comment on the stability of the system for this fault.

SOLUTION:

# Computation of stator current

It = S* / E * T    = (0.9-j0.436) / 1.0    = 0.9- j0.436

# Computation of the terminal voltage

E’ = Et + jXd’It     = 1.1305 + j0.27

# Computation of infinite bus voltage

EB = Et –Jx4(i4+Ji)

X4 = Xtr + X3  = 0.47 p.u.

Ir = P / Et = 0.9 p.u.

I = -Q / E = - 0.435p.u.

Eb = 0.7933-j0.4275

Computation of angle of separation between E’ and Eb

δ = ∟E1’ - ∟Eb = 0.7282 rad

If the infinite bus is taken as reference then

E’ = 1.16 ∟41074

It = 0.99∟2.52    Et =1∟28.31

Critical clearing angle:

Cosδ = {PM(δMAX – δ0) + P3MAXcosδMAX – P2MAXcosδ0 } / { P3MAX – P2MAX}

P3MAX = Eb E’ / (Xd’ + Xtr + Xline-1)      = 1.098

P2MAX = 0

To find δMAX :

### After the fault clearance

δMAX = 180 – sin-1 (Pe / P3max) = 124.94 degree = 2.18 rad

##### Substituting in the above formula

Cos δc = (0.9(2.18-0.728) + 1.09 * cos124.94)/1.09

δc = 51.88 deg = 0.905 rad

To find critical clearing time:

Tc = (2H(δc – δ0)) /  f0 PM = 0.085s

b) Simulate the above sequence of fault occurrence and clearance using the

Software available and plot the swing curve (rotor angle versus time) as

well as the curves showing angular velocity and real power delivered by

the plant versus time

(c)    Determine the critical clearing angle and time for the above fault through

trial and error method by repeating the simulation in (b) for different fault

clearing times and compare the critical clearing angle and time obtained.(case2)

Case 3:

Three-phase-to-ground fault at the mid point of line 2 occurs at t=0 sec and is

cleared at t=0.07 sec by the simultaneous opening of two breakers in line 2.

Comment on the transient stability of the system under case 2 and case 3 and

compare the severity of the faults; cases 1,2 and 3 from the point of view of

maximum rotor swing and also by comparing the clearing time margin available.

3.         Determine the steady-state stability margin (MW) available for the system

under the given operating condition in exercise 6.5.1. Also determine the

transient stability margin (MW) available for the operating condition given in

exercise 6.5.1. for the three cases of fault, case 1, case 2 and case 3. Can the

severity of the fault be measured using this margin?

Steady state stability margin = (Pmax – P0)* base .MW.

Pmax = EV / X = E’ Eb / X

= 1.16 * 0.9 / (0.328 + 0.3 + 0.15 )

= 1.347 M.W.

Substituting the value in the above formula

Stability margin = (1.347 – 0.9) * 2220

= 992.34 M.W.

Transient stability margin  = (Pmax (stable) – P0) M.W.

4.         Is proposed to examine the small-signal stability characteristics of the

system given in exercise 1. about the steady-state operating condition

following the loss of line 2; Assume the damping coefficient KD = 1.5 p.u

torque / p.u speed deviation.

(a) Write the linearized swing equation of the system. Obtain the

characteristic equation, its roots, damped frequency of oscillation in Hz,

damping ratio and undamped natural frequency. Obtain also the force-free

time response  Δδ (t) for an aintial condition perturbation Δδ = 5 degree and          Δω(t) = 0.

5.         Repeat the small-signal stability analysis carried out using the software

package in exercise 4 with the following parameters and comment on the

relative stability of each case:

(a) KD = 0 p.u and –1.5 p.u

(b) KD = 1.5 p.u but with P = 1.2, 1.5 and 2.0 p.u

EXPERIMENT 7

TRANSIENT STABILITY ANALYSIS OF MULTIMACHINE POWER SYSTEMS

AIM:

(i) To become familiar with modelling aspects of synchronous machines and network for

transient stability analysis of multi-machine power systems.

(ii) To become familiar with the state-of-the-art algorithm for simplified transient stability

simulation involving only classical machine models for synchronous machines.

(iii) To understand system behaviour when subjected to large disturbances in the presence of

synchronous machine controllers.

(iv) To become proficient in the usage of the software to tackle real life problems

encountered in the areas of power system planning and operation.

# OBJECTIVES

(i) To assess the transient stability of a multimachine power system when subjected to a

common disturbance sequence: fault application on a transmission line followed by fault

removal and line opening.

(ii) To determine the critical clearing time.

(iii) To observe system response and understand its behaviour during a full load rejection at a

substation with and without controllers.

(iv) To observe system response and understand its behaviour during loss of a major

generating station.

(v) To understand machine and system behaviour during loss of excitation.

(vi) To study the effect of load relief provided by under frequency load shedding scheme.

SOFTWARE REQUIRED

MULTIMACHINE TRANSIENT STABILITY module of AU Power lab or equivalent

EXERCISES

1.. Transient stability analysis of a 9-bus, 3-machine, 60 Hz power system  with the following system modelling requirements:

i. Classical model for all synchronous machines, models for excitation and speed

governing systems not included.

(a) Simulate a three-phase fault at the end of the line from bus 5 to bus 7 near bus 7 at time = 0.0 sec. Assume that the fault is cleared successfully by opening the line 5-7 after 5 cycles

( 0.083 sec) . Observe the system for 2.0 seconds

(b) Obtain the following time domain plots:

- Relative angles of machines 2 and 3 with respect to machine 1

- Angular speed deviations of machines 1, 2 and 3 from synchronous speed

- Active power variation of machines 1, 2 and 3.

(c) Determine the critical clearing time by progressively increasing the fault clearing

time.

EXPERIMENT 8

ELECTROMAGNETIC TRANSIENTS IN POWER SYSTEMS

AIM:

- To study and understand the electromagnetic transient phenomena in power systems caused due to switching and fault by using Electromagnetic Transients Program (EMTP).

- To become proficient in the usage of EMTP to address problems in the areas of over voltage protection and mitigation and insulation coordination of EHV systems.

OBJECTIVES:

- To study the transients due to energization of a single-phase and three-phase load from a non-ideal source with line represented by Π – model.

- To study the transients due to energization of a single-phase and three-phase load from a non-ideal source and line represented by distributed parameters.

- To study the transient over voltages due to faults for a SLG fault at far end of a line.

- To study the Transient Recovery Voltage (TRV) associated with a breaker for a three-phase fault.

SOFTWARE REQUIRED: 	ELECTROMAGNETIC TRANSIENTS PROGRAM –

UBC version module of AU Power lab or equivalent

EXCERCISE:

Prepare the data for the network given in the Annexure and run EMTP. Obtain the plots of source voltage, load bus voltage and load current following the Energization of a single-phase load. Comment on the results. Double the source inductance and obtain the plots of the variables mentioned earlier. Comment on the effect of doubling the source inductance.

Energization of a single phase 0.95 pf load from a non ideal source and a more realistic line representation (lumped R, L, C):

Circuit Diagram:

Exercise

1 Prepare the data for the network given in the Annexure 8.1 and run EMTP. Obtain the plots of source voltage, load bus voltage and load current following the energisation of a single-phase load and obtain the plots

Output

2. Prepare the data for the network given in the Annexure 8.2 and run EMTP. Obtain the plots of voltages of phases a, b, c at the load bus and switch A current of phase a following energisation of the three-phase load by closing the switches simultaneously.

Output

3. Prepare the data for the network given in the Annexure 8.3 and run EMTP. Obtain the plots of voltages at source, Bus 1 and Bus 12 following the energisation of the single phase open ended line represented by distributed parameters. Obtain the plot of voltage at Bus 12 by expanding the time scale by a factor of ten, i.e, plot the voltage for the first 2.5 millisecond.

Output

4 Prepare the data for energisation of a three-phase load fed by a three-phase distributed parameter line as given in the Annexure 8.4 and run EMTP. Obtain the plots of voltages at source, Bus 1 and phase a voltage at Bus 12 following the energisation by simultaneous closing of all the three phases

Output

5 Prepare the data for the network given in the Annexure 8.5 and run EMTP. Obtain the plots of voltages at source, Bus 1 and Bus 2 following a single lineto- ground fault at the far end, Bus 2.

Output

6. Prepare the data for the network given in Annexure 8.6 and run EMTP. Obtain the transient recovery voltage (TRV) in each phase for a three-phase fault at Bus 1. The TRVs are the voltages across the switches between Bus1 and BKR1.

Output

INPUT DATA:

ENERGIZATION OF LOAD-EMTP EXPERIMENT NO: 1

.5E-4     .5E-1 -1     1

SRC  BUS1		.0	6.0	.0

BUS1 BUS12      	.05   	2.0    	.0

BUS1             		.0      	.0    	.81

BUS12            		.0      	.0    	.84

BUS12BUS13S      	.0     	6.0    	.0

BUS13L         		22.61   	19.72   	.0

BUS13SBUS13L    	 .1E-2	.9999E+4                  1

14   SRC 1  		.5634E+2      .60E+2	.0E+0      -.1E+1  .9999E+4

SRCBUS13L

EXPERIMENT 9

LOAD-FREQUENCY DYNAMICS OF SINGLE-AREA AND TWO AREA POWER SYSTEMS

AIM:

To become familiar with the modeling and analysis of load-frequency and tie-line flow dynamics of a power system with load-frequency controller (LFC) under different control modes and to design improved controllers to obtain the best system response.

OBJECTIVES:

- To study the time response (both steady state and transient) of area frequency deviation    and transient power output change of regulating generator following a small load change in a single-area power system with the regulating generator under “free governor action”, for different operating conditions and different system parameters.

- To study the time response (both steady state and transient) of area frequency deviation and turbine power output change of regulating generator following a small load change in a single- area power system provided with an integral frequency controller, to study the effect of changing the gain of the controller and to select the best gain for the controller to obtain the best response.

- To analyze the time response of area frequency deviations and net interchange deviation following a small load change in one of the areas in an inter connected two-area power system under different control modes, to study the effect of changes in controller parameters on the response and to select the optimal set of parameters for the controller to obtain the best response under different operating conditions.

SOFTWARE REQUIRED:

‘LOAD FREQUENCY CONTROL’ module of AU Power Lab or equivalent

EXERCISES

1. It is proposed to simulate using the software available the load-frequency dynamics of a single-area power system whose data are given below:

Rated capacity of the area = 2000 MW

Normal operating load = 1000 MW

Nominal frequency = 50 Hz

Inertia constant of the area = 5.0 s

Speed regulation (governor droop)

of all regulating generators = 4 percent

Governor time constant = 0.08 s

Turbine time constant = 0.3 s

Assume linear load–frequency characteristics which means the connected system load increases by one percent if the system frequency increases by one percent. The area has a governor control but not a load-frequency controller. The area is subjected to a load increase of 20 MW.

(a) Simulate the load-frequency dynamics of this area using available software and check the following:

(i) Steady – state frequency deviation fs in Hz. Compare it with the hand-calculated value using “Area Frequency Response Coefficient” (AFRC).

(ii) Plot the time response of frequency deviation f in Hz and change in turbine power PT in p.u MW upto 20 sec. What is value of the peak overshoot in f?

(b) Repeat the simulation with the following changes in operating condition, plot the time

response of f and compare the steady-state error and peak overshoot.

(i) Speed regulation = 3 percent

(ii) Normal operating load = 1500 MW

Hz

MANUAL CALCULATION: A)LOAD FREQ SINGLE AREA- PROBLEM 1(a)

Steady State frequency deviation   Δfs=-(M/) Hz

where

=Area Frequency Response Coefficient(AFRC)=D+(1/R) Hz/p.u.M.W.

M is in p.u.MW =20/2000=0.01 p.u.MW/Hz

D=1100∗10001100∗50=20MWHz  		 D =20/2000=0.01 p.u.MW/Hz

1R=20004100∗50=1000MWHz		1/R=1000/2000=0.5 p.u.MW/Hz

=0.01+0.5=0.51 p.u MW/Hz

Δfs = -(M/)Hz      = -(0.01)/(0.51)

Δfs = -0.0196 Hz

MANUAL CALCULATION: B)LOAD FREQ SINGLE AREA- PROBLEM 1(b)

Steady State frequency deviation   Δfs=-(M/) Hz

where

=Area Frequency Response Coefficient(AFRC)=D+(1/R) Hz/p.u.M.W.

M is in p.u.MW =20/2000=0.01 p.u.MW/Hz

D=1100∗15001100∗50=30MWHz  		 D =30/2000=0.015 p.u.MW/Hz

1R=20003100∗50=1333MWHz		1/R=1333/2000=0.666 p.u.MW/Hz

=0.015+0.666=0.681 p.u MW/Hz

Δfs = -(M/)Hz      = -(0.01)/(0.681)

Δfs = -0.01467 Hz

COMPARISON OF A AND B:

| D | R | Δfs Hz | Δf peak Hz |
| --- | --- | --- | --- |
| 0.01 | 4% | -0.0196 | -0.0256 |
| 0.015 | 3% | -0.0155 | -0.0215 |

2. Assume that the single-area power system given in exercise 9.5.1 is provided with a load frequency controller (an integral controller) whose gain KI can be tuned.

(a) Carryout the simulation for the same disturbance of load change of 20 MW for different values of KI, obtain the time response f for each case, critically compare these responses and comment on their suitability for practical application.

9-13

(Hint: For choosing different values of KI, first set the governor and turbine time

constants to zero and determine analytically the value of integral gain KI,cr to have

critical damping on the response f (t). Choose the range of KI to include

KI,cr as 0 KI ( KI,cr + 1.0 ) )

(b) From the investigations made in (a) above, choose the best value of KI which gives an “optimal” response f (t) with regard to peak overshoot, settling time, steady-state error and Mean Sum- Squared-Error (MSSE).

3 It is proposed to simulate the load frequency dynamics of a two-area power system. Both the areas are identical and has the system parameters given in exercise 9.5.1. Assume that the tie-line has a capacity of Pmax 1-2 = 200 MW and is operating at a power angle of ( 01- 20 ) = 300. Assume that both the areas do not have load –frequency controller. Area 2 is subjected to a load increase of 20 MW.

(a) Simulate the load-frequency dynamics of this system using available software and

check the following:(i). Steady-State frequency deviation fs in Hz and tie-line flow deviation, P12,S inp.u. MW. Compare them with hand-calculated values using AFRC’s

(ii) Compare result fs with that obtained in single area simulation in exercise 1

(a), and comment on the support received from area 1 and the advantages of

interconnecting with neighbouring areas .

(iii) Plot the time responses, f1(t), f2 (t), PT1(t) , PT2(t) and P12(t). Comment

on the peak overshoot of f1, and f2.

MANUAL CALCULATION:TWO AREA LOAD FREQUENCY CONTROL PROGRAM OUTPUT

Δfs  = -(M1+M2)/( 1+2)

M1 =0;M2=0.01 p.u .MW/Hz

1  =2=0.51 p.u .MW/Hz (identical areas)

Δfs = - (0.01)/(0.51+0.51)= - 0.0098 Hz

ΔP1-2s = - ΔP1-2s = ( 1M2- 2M1)/ ( 1+2) p.u .MW

= (0.51*0.01)/(0.51+0.51)

= 10 MW.

Comparison of manual calculation and simulated values.

| MANUALY CALCULATED VALUES | SIMULATED VALUES |
| --- | --- |
| Δfs = - 0.0098 Hz |  |
| ΔP1-2s=10MW |  |

EXPERIMENT 10

# ECONOMIC DISPATCH IN POWER SYSTEM

# AIM:

To understand the basics of the problem of Economic Dispatch of optimally adjusting the generation schedules of thermal generating units to meet the system load which are required for unit commitment & Economic operation of power systems.

To understand the development of co-ordination equation (the mathematical model for ED) without and with losses & operating constraints and solution of these equations using direct and iterative methods.

# OBJECTIVE:

- To write a program for solving ED problem without and with transmission losses for a given load condition/daily load cycle using

(a)Direct method

(b)Lambda-iteration method

- To study the effect of reduction in operation cost resulting due to changing from simple load dispatch to economic load dispatch.

- To study the effect of change in fuel cost on the economic dispatch for a given load.

- To study the use of ED in finalizing the unit commitment for tomorrow’s operating conditions of power system.

# EXERCISE:

# 1. The system load in a power system varies from 250MW to 1250MW. Two thermal units are operating at all times and meeting the system load. Incremental fuel cost in hundreds of rupees per Megawatt hour for the units are

dF1/dP1 = 0.0056P1 + 5.6   ;           P1 in MW

dF2/dP2 =  0.0067P2 + 4.5  ;           P2 in MW

The operating limits of both the units are given by

100<=P1, P2<=625MW

Assume that the transmission loss is negligible.

- Determine the economic (minimum fuel cost) generation schedule of each unit, the incremental fuel cost of each unit and the incremental cost of received power for different load levels from 250 to 1250MW in steps of 100MW.

- Draw the following characteristics from the results obtained in (a)

  - Incremental cost of received power in hundreds of rupees per MW hr  versus system load in MW.

  - Unit outputs P1 and P2 in MW versus system load in MW.

- Determine the saving in fuel cost in hundreds of rupees per hour for the economic distribution of a total load of 550MW between the two units compared with equal distribution of that load between the two units.

# INPUT:

Economic Dispatch - Lambda Iteration Method Without Loss

AU Power lab

VII

0.001 0.05    10

2  $/hr  $/MWhr

0.0028 5.6 0 100 625

0.00335 4.5 0 100 625

1

250 1250 100

# OUTPUT:

Manual Calculation:

 = (PD + b1/2a1 +b2/2a2)/(1/2a1+1/2a2)

For PD = 550 MW

= 550 + ((5.6/0.0056 + 4.5/0.0067)/(1/0.0056 + 1/0.0067))

-  = 6.77691 Rs MW/Hr

PG1* = -b1/2a1 = (6.77691-5.6)/0.0056 = 210.626 MW

PG2* = -b2/2a2 = (6.77691-4.5)/0.0067 = 339.8374 MW

Fuel Cost:

FC1 = 0.0028 PG12 + 5.6 PG1 + C1 Rs/Hr

FC2 = 0.00335 PG12 + 4.5 PG1 + C2 Rs/Hr

Where C1 & C2 are unknown constants

Fuel Cost for optimal schedule (PG1*, PG2*)

FC1 = 0.0028(210.1626) 2+5.6(210.1626) + C1 Rs/Hr

FC2 = 0.00335(339.8374) 2 + 4.5(339.8374) + C2 Rs/Hr

FC*=FC1+FC2=3216.74+C1C2 Rs/Hr

Fuel Cost for equal Sharing: [PG1 = 275 = PG2]

FC1 = 0.0028(275) 2+5.6(275) + C1 Rs/Hr

FC2 = 0.00335(275) 2 + 4.5(275) + C2 Rs/Hr

FC1 + FC2 = 3242.59 + C1C2 Rs/Hr

Total Saving:

FC = FC – FC* = 3242.59 – 3216.74 = 25.85 Rs/Hr

### EXERCISE :

2. For the system in exercise 4.3 take into account the transmission loss.

- Determine the economic loading of each unit to meet a total customer load of 550MW, using the program developed in 4.2

- What is transmission loss of the system at the economic loading?

- Determine the penalty factor for each unit and the incremental fuel cost at each generating bus.

- Determine also the incremental cost of received power (or system ).Assume that the loss coefficient in per unit on a 100MVA base of customer load level of 550MW are given by

#### B11 = 0.008383183

B12 = B21 = -0.000049448

B10/2 = 0.000375082

B22 = 0.005963568

B20/2 = 0.000194971

B00 = 0.000090121

### INPUT:

Economic Dispatch - Lambda Iteration Method With Loss

AU Powerlab

2001399126

VII

0.01  0.05  10

2  $/hr   $/MWhr

0.0028 5.6 0 100 625

0.00335 4.5 0 100 625

0.008383183 -0.000049448

- 0.000049448 0.005963568

0.000375082 0.000194971

0.000090121 100

0

550OUTPUT :

Manual Calculation:

### B11 = 8.38*10-3

B12 = -0.049*10-3

B21 = 0

B22 = 5.96*10-3

PL = B11P12 + P22B22 + P1P2B12

PD = P1 + P2 – PL

PD = 550 MW

 = (550 + 5.6/0.0056 + 4.5/0.0067) / (1/0.0056 + 1/0.0067)

  = 6.7767 Rs/MW-Hr

For First Iteration

Assume P2 = 0

P1 = [1-(b1/)-(2B12P2)]/[(2a1/)+2B11]

### P1 = [1-(5.6/6.776)-0]/[(0.0056/6.776)+0.01676]

### P1 = 9.8686 MW

P2 = [1-(b2/)-(2B21P1)]/[(2a2/)+2B22]

### P2 = [1-(4.5/6.776)-0]/[(0.0067/6.776)+0.01192]

### P2 = 23.02 MW

#### PL = P12B11 + P22B22 + P1P2B12

= [(9.8686)2*(0.00838) + (26.02)2*(0.00596) + 9.8686*26.02*-0.049*10-3]

### PL = 4.8387 MW

#### PD = P1 + P2 – PL

= 9.8686 + 26.02 – 4.838

### PD = 31.04 MW

: 3292.06  $/hr

### EXERCISE :

- A power system with negligible transmission loss, the system load varies from a peak of 1200MW to a valley of 500MW. There are three thermal generating units which can be committed to take the system load. The fuel cost data and generation operation limit data are given below

In hundreds of rupees per hour:

F1 = 392.7 + 5.544P1 + 0.001093P12 ;           P1 in MW

F2 = 217.0 + 5.495P2 + 0.001358P22 ;           P2 in MW

F3 = 65.5 + 6.695P3 + 0.004049P32  ;             P3 in MW

Generation Limit:

150<=P1<=600 MW

100<=P2<=400 MW

50<=P3<=200 MW

There are no other constant on system operation. Obtain an optimum (minimum fuel cost) with commitment table for each load level taken in steps of 100 MW from 1200 to 500.Adopt “Brute force enumeration” technique. For each load level obtain economic schedule using economic dispatch program developed in ex 4.3 for each feasible combination of units and choose the lowest fuel cost schedule among the combination.

Show the details of economic schedule and the component and total cost of operation for each feasible combination of unit for the load level of 900MW.

### INPUT:

Economic Dispatch - Lambda Iteration Method

Without Loss

AU Power lab

2003557

VII

0.001 0.05    5

3	   $/hr	   $/MWhr

0.001093 5.544 392.7 150 600

0.001358 5.495 217.0 100 400

0.004049 6.695 65.50 50 200

1

500 1200 100